PRODUCT DATA

GREENTECH PT2701-F

BOILER WATER TREATMENT

DESCRIPTION AND USE

The GREENTECH PT2701-F product is a proprietary liquid blend containing “Purified Tannin Technology” and an effective boiler water antifoam.  The product is designed to provide corrosion and deposit control of the pre-boiler and boiler surfaces.  This GREENTECH product in combination with good feedwater quality, proper control of boiler blowdown and optimum recovery of steam/condensate will help ensure optimum boiler system performance and greatly reduce fuel usage.  This product offers a more environmentally friendly and energy efficient option when compared to conventional boiler treatment programs.

The GREENTECH PT2701-F inhibitor/dispersant package utilizes a proven “Purified Tannin Technology”.  This unique component has demonstrated effective deposit control of metal oxides and hardness salts with the ability to remove existing scale.  Additionally, this same component acts as an oxygen scavenger and inhibitor to protect the preboiler and boiler from oxygen-related corrosion.  The active product residual is easily measured providing a feed control test to assist in maintaining proper feed concentration.  This product has successfully been used at boiler pressure between 5 psig and 1000 psig.  GREENTECH PT2701-F is acceptable for applications that require compliance with FDA regulations for direct food contact.

CHEMICAL FEEDING AND CONTROL

GREENTECH PT2701-F is typically fed continuously paced proportional to feedwater and/or makeup flow and adjusted based on maintaining a target residual in the boiler.  Typically the product is dosed at 1.0 ounces to 9.0 ounces/1000 gallons of feedwater.  Increased dose may be required to clean dirty boiler surfaces.  The specific dosage varies depending upon system operating conditions and will be specified by the technical representative servicing the facility.  On rare occasion, alkalinity boost may be required.

The product may be fed neat (directly from the shipping container) or fed pre-diluted (with softened or better quality water) from a mix tank.  Normal materials of construction for the chemical feed system include stainless steel and plastics. Avoid using copper and aluminum materials.  Product MUST be fed with an injection quill beneath the normal water level.

TYPICAL PROPERTIES

Appearance	Opaque black liquid

Odor	Characteristic odor

Flash Point	None

Specific gravity @22ºC	1.045 - 1.055

pH (undiluted)	12.5 - 13.0

Freeze Point	< -3ºC (26ºF)

SAFETY AND HANDLING

Do not take internally and avoid contact with eye and skin.  If ingested, drink at least two (2) glasses of water and get medical attention.  Contact with eyes should be avoided.  If eyes are contacted, flush immediately with clean water for 15 minutes and get medical attention.  Avoid skin contact, immediately wash with soap and water.  For additional information, see the Material Safety Data Sheet provided with this product.

PACKAGING

GREENTECH PT2701-F is packaged in 55, 30, 15, and 5 gallon plastic containers and one-way 275 gallon totes.