# PRODUCT DATA

# COOLING LAY-UP 1982

# COOLING & PROCESS CORROSION INHIBITOR

# DESCRIPTION AND USE

Cooling Lay-up 1982 is a vapor phase corrosion inhibitor (VpCI) formulation, packaged in a convenient liquid form and is used for seasonal or long-term lay-up of cooling and process water systems.  This liquid formulation is free of phosphates, heavy metals, nitrite and oil-based components.  Cooling Lay-up 1982 is specifically designed to be recirculated in the cooling loop or process water loop and will protect the entire system, whether laid-up flooded, partially flooded or drained, for up to two years.  The VpCIs vaporize from the liquid lay-up solution into the system’s air space ensuring metal protection in the vapor phase, liquid phase and at the vapor/liquid interface.  Distribution requires circulation of lay-up solution.

APPLICATION AND TREATMENT REQUIREMENTS

Cooling Lay-up 1982 can be added directly to the system after it has been removed from service, but while it is still flooded with water. Preferably, the system is drained and flushed of any sludge before adding the proper amount of Cooling Lay-up 1982.  Circulation of the treatment solution for 12 – 24 hours is recommended to achieve some mixing of the VpCIs in solution throughout the system.  Roughly two gallons this product is sufficient to treat 1000 gallons of total system volume.

During lay-up the system should be sealed tightly to hold in the VpCIs.  Lay-up can be effective for up to two years. The system can be brought online immediate while still containing the VpCI solution.  Product concentration can be measured using a nitrate test.  A calibration curve is available upon request.  Check with your technical representative for specific application guidelines.

# TYPICAL PROPERTIES

Appearance	Clear to amber liquid

Odor	Mild organic amine odor

Specific gravity	1.13 – 1.14

pH (1% Solution)	8.5 – 9.5

# SAFETY AND HANDLING

Cooling Lay-up 1982 may be toxic in concentrated form.  DO NOT take internally.  If ingested drink several glasses of water or milk and induce vomiting, if patient is conscious.   Get medical attention.  Minimize exposure/contact with product by wearing protective gloves and glasses.  If in contact, minor irritation may occur.  Rinse liquid from exposed parts with water and get medical attention if irritation persists.  For additional information, see the Material Safety Data Sheet provided with this product.

# PACKAGING

Cooling Lay-up 1982 is packaged in 55 gallon plastic drums and 5 gallon plastic pails.